# Town of Andover

Town Offices

36 Bartlet Street

Andover, MA  01810

(978) 623-8620

www.andoverma.gov

DATE:	June 3, 2022

TO:		Jacki Byerley, Town Planner

FROM:	Chris Clemente, Building Inspector

CC:		Planning Board

RE: 		1320 South St. Battery Project

An IDR was held on this project on 4/12/2022 & 5/10/2022. Multiple concerns were discussed and remain outstanding as follows:

- Adequacy of fire protection – Applicant has proposed a 1500-gallon tank. Applicant has not elaborated on how the size of this tank was determined. AFR feels that this would be completely inadequate should any sort of fire event occur at the site.

- Water supply for Fire Protection – where is fire protection water coming from? Is there an agreement with the Town of Tewksbury in place?

- Addressable Fire Alarm/Panel – Applicant has not shared details of alarm/master box. How will panel be addressed? Specific batteries or just a general alarm? Notification sequence etc?

- Noise and decibel levels- Applicant has not furnished any information on potential noise levels.

- Sound absorbing wall- Applicant has not furnished any details on size, height, materials of wall.

- Construction traffic and the queuing of tractor trailers delivering Conex/Batteries to site – Applicant was requested to supply some sort of plan or agreement for staging deliveries vs having traffic queuing up on South St.

- Disposal or abandonment of site- The technology is evolving rapidly. Given that the life cycle of these batteries is 5-7 years what happens when the facility has reached the end of its life span or the corporate entity is sold, dissolved or bankrupt?  The Town does not want to be left with a hazardous site and must incur cleanup costs. Consider having applicant post some sort of surety bond or insurance to cover any removal costs and impose some sort of conditions similar to Article VIII § 6.1.8 & 6.1.9 requiring surety bond and removal within 1 year of cessation of use.

- Applicant to provide locations of other installations- Staff requested locations of other installations to view/consult with other municipalities which have permitted these facilities. To date this information has not been provided.